## Assumptions
DIABLO 400 PoC — BOM-001 Rev 0.3 — Configuration Assumptions
Basis: OCP Diablo 400 Base Specification v0.7.0 (Effective March 1, 2026). Single power rack PoC. All pricing ROM (Rough Order of Magnitude), June 2026, budgetary only — confirm with vendor quotes.
INPUTS (edit blue cells)
Target rack average DC output (kW) | 1000 | Spec §7.3.2 range 800 kW – 1.1 MW (Table 5)
AC/DC PSU rating (kW) | 27 | Table 10, Solution 2 @ 480 VAC
PSUs per 2OU power shelf | 6 | Spec §8.2 "various numbers"; 6 matches Delta 108 kW shelf precedent
Shelf redundancy (+N shelves) | 1 | Designer choice; spec §5 allows redundancy schemes
DC output cable rating (kW) | 100 | Spec §8.1.3 Option 2: 100 kW / 125 A per cable
DC PDU module rating (kW) | 400 | Spec §8.1.3: up to 400 kW per Output Protection & Control Module
AC input voltage (V, 3-phase) | 480 | Table 2, Nominal1
AC tap / cord rating (A) | 200 | Spec §8.1.1: up to 12x 200 A cords
End-to-end efficiency @100% load | 97% | Table 9 minimum >97% @ 480 VAC, 50% load; >96.5% @100%
BBU unit power rating (kW) | 80 | Delta GTC 2026 80 kW embedded BBU class (sampling)
Contingency on ROM total | 15% | Pre-1.0 spec + sampling hardware = high uncertainty
DERIVED (formulas — do not edit)
Power shelf count (incl. +N) | 8 | Shelves to cover target power, plus redundancy
PSU module count | 48 | Shelves x PSUs per shelf
Installed shelf capacity (kW) | 1296 | Check vs target
DC output cables (qty) | 10 | 100 kW cables to carry target power
DC PDU modules (qty) | 3 | 400 kW modules
AC tap kVA each | 166.2769 | 480 V x 200 A x sqrt(3)
AC 200 A feeds (qty) | 7 | DC out / efficiency / tap kVA. Spec max 12 (§8.1.1)
BBU units for 100% load backup (qty) | 13 | Power-matched per §7.2.1.1 (45–90 s @ 100% load). OPTIONAL

## BOM
Item | Description | Spec Ref | Vendor / Part Family | Status | Qty | Unit | ROM Unit ($) | Ext. ($) | Lead Time | Notes / Alternates
A — RACK MECHANICAL (§6)
A1 | ORV3 rack frame, 48OU, 21-in, ~2329 mm H x 600 mm W x 1200 mm D | §6 | Eaton EORV49RU48B / Rittal ORV3 / Legrand / ATEN RC8000 | Production | 1 | ea | 8000 | 8000 | 8-12 wk | Std ORV3 static rating ~1,600 kg (~3,500 lb) — BELOW 6,000 lb spec target. Reinforced/bespoke frame needed for full compliance.
A2 | Frame reinforcement + custom mods: sliding shelves, blind-mate rails (PSU/BBU/CBU), center-justified busbar mounting | §6.1 | Custom fab (Rittal/Legrand bespoke or local) | Custom Fab | 1 | lot | 15000 | 15000 | 10-14 wk | Blind-mate sliding shelf scheme is non-standard vs 48V ORV3 single-busbar layout.
A3 | Locking safety doors front/rear, partial or full, intrusion switch + emergency shutoff option | §6.1, §11 | Rack vendor option / custom | Custom Fab | 1 | set | 2500 | 2500 | w/ frame | Door pressure drop must be in fan sizing budget (§10.2).
A4 | Side panels / airflow containment, front-to-back | §10.2 | Rack vendor | Production | 1 | set | 1200 | 1200 | w/ frame
A5 | Casters, leveling feet, seismic anchoring kit | §6, §11 | Rack vendor | Production | 1 | set | 800 | 800 | w/ frame | Stability: no tip-over at 10 deg tilt (§11.1).
B — AC INPUT & AC PDU (§7.1, §8.1.1, App D)
B1 | Busway tap-off box, 480 V 3-ph, 200 A, fused | §15.1 | Starline / PDU Cables UL857 tap box | Production | 7 | ea | 3500 | 24500 | 6-10 wk | Tap-box or MTS per App D. Qty derived; spec cap 12x200A.
B2 | 200 A AC whip, 4x1C 3/0 AWG W-type, ~15 m, Molex 1x4 ferrule or lugs | §15.1, Tbl 14 | Custom assembly (PDU Cables etc.) | Custom Fab | 7 | ea | 2200 | 15400 | 4-8 wk | Molex 1x4 connector P/N not verified at catalog level — confirm w/ Molex or use lugs.
B3 | AC PDU panel: up to 12x 200 A inputs, protection fuses, 2-hole lugs or connectorized, output split to shelf feeds (e.g. 200A->4x50A) | §8.1.1 | Custom / ODM build (no catalog item) | Custom Fab | 1 | ea | 18000 | 18000 | 12-16 wk | No purpose-built Diablo AC PDU on market. Assemble from stock fuse blocks + panel, or ODM.
B4 | Quick-connect input option: SurLok Plus 1 kV, 120-200 A class | §6.1, App D | Amphenol SurLok Plus (e.g. SLPPA series) | Production | 16 | ea | 95 | 1520 | stock-4 wk | Spec names "SurLock" — actual family is SurLok/SurLok Plus. UL1977, RADSOK contacts.
B5 | AC PDU-to-power-shelf output cables, 60 A or 100 A, 2 AWG W-type | §8.1.1, §15.1 | Custom assembly | Custom Fab | 8 | ea | 450 | 3600 | 4-6 wk | One feed per shelf assumed; connectors per PSU vendor requirement (§8.2).
C — AC/DC POWER SHELVES & PSUs (§8.2, Tbl 10)
C1 | Power shelf 2OU, 21-24 in, 3-ph AC in, +/-400 VDC out, droop + active current share, bus clip w/ thermal sensor | §8.2 | Delta 108 kW HVDC shelf class / Lite-On / Flex | Sampling | 8 | ea | 4500 | 36000 | eval agmt | CRITICAL LONG-LEAD. Not in distribution — sampling/eval agreement required. ROM estimate only. Load-side target per LVDC WP §3.1: HPR v4 100 kW DC-input shelf (1OU, +39% density vs 72 kW AC HPR v2).
C2 | AC/DC PSU module, 1OU, 27 kW @480 VAC, +/-400 VDC 3-wire galvanically isolated, hot-swap | §8.2.1, Tbl 10 | Delta 18.5 kW (GTC26) / Lite-On / Flex — 27 kW class per Tbl 10 Sol.2 | Sampling | 48 | ea | 3000 | 144000 | eval agmt | Must meet 410->400 V droop (10V +/-0.5V), +/-0.5% reg, 150-180% TDP transient, 1 A/us slew, 20 ms holdup (§7.1.3.1, §7.3). No vendor-verified full compliance yet.
C3 | Shelf control module (Redfish/Modbus PMC) | §8.2.2, §9 | Advanced Energy ORv3 PMC class / vendor PMC | Production | 8 | ea | 600 | 4800 | 4-8 wk | MSFT RSCM / Google module are hyperscaler-internal; use vendor PMC for PoC.
D — +/-400VDC DISTRIBUTION BUSBAR (§8.3)
D1 | Custom vertical 3-conductor busbar (+400 / COM / -400), full rack height, 1.1 MW, air-cooled, touch-safe covers, center-justified | §8.3, §6.1 | Storm Power / Methode / Mersen / Rogers ROLINX (custom) | Custom Fab | 1 | ea | 12000 | 12000 | 10-16 wk | NO catalog 3-conductor +/-400V ORV3 busbar exists. Includes NRE/engineering. Existing ORV3 bars are single-conductor 48 V.
D2 | Busbar HiPot / insulation test + report (>=2x working voltage) | §11.1 | Fab shop or test lab | Service | 1 | lot | 2500 | 2500 | w/ busbar | Stage-gate item before energization.
E — DC PDU / OUTPUT PROTECTION & CONTROL (§8.1.3)
E1 | DC PDU module chassis, 400 kW class: enclosure, busbar attach, output connector panel, integration | §8.1.3 | Custom integration (no catalog item) | Custom Fab | 3 | ea | 8000 | 24000 | 12-16 wk | Assembled from E2-E6 components. Delta SiC e-Fuse shown but not catalog.
E2 | DC fuse, 1000 VDC, 125-160 A class | §8.1.3, §11.1 | Mersen NH gBat / Eaton Bussmann XL-NH | Production | 24 | ea | 85 | 2040 | stock-6 wk | 2 poles per output cable + spares. IEC 60269-7 battery/PV lines, to 150 kA interrupt. Shelf spec §4.1.1 fixes PDU protection at 2x 80A fuses per 100kW 2-cord shelf — use 80A class per 50kW feed.
E3 | DC contactor/relay, 800-1000 VDC, 150 A class | §8.1.3 | TE Kilovac EV200/ECK / Gigavac GX / Sensata / Panasonic EV | Production | 20 | ea | 320 | 6400 | 8-20 wk | EV-grade. Gigavac lead times reportedly long post-Sensata acquisition — order early.
E4 | Ground fault detector / insulation monitor w/ voltage-balance detection (HRG midpoint) | §8.1.4.1.1 | Bender ISOMETER iso685 / isoES425 / iso415R | Production | 10 | ea | 1800 | 18000 | 4-8 wk | Spec requires GFD per output cable for HRG. DESIGN STEER (OCP DCF LVDC WP v1.0 §6.4.1): industry classifies Mt. Diablo as 350/700V Bipolar TN-S w/ distributed M — SOLID midpoint ground, under which GFD is optional per Diablo §8.1.4.2 (~$18K de-scope). Keep >=1 unit for insulation monitoring.
E5 | Per-output ON/OFF switches, LED indicators, signal wiring, relay drivers | §8.1.3 | Stock industrial (panel-mount) | Production | 1 | lot | 1500 | 1500 | stock | Output voltage disconnect before unplug — no live contacts.
E6 | HRG resistor assembly, midpoint-to-PE, concealed/touch-safe | §8.1.4.1 | Stock power resistors / custom mount | Custom Fab | 1 | ea | 400 | 400 | 2-4 wk | Only if HRG selected. LVDC WP steer is TN-S solid midpoint bond (zero-ohm) — replaces resistor w/ fault-current-rated bonding jumper per Diablo §8.1.4.2 (easier fault ID, fuse-based clearing).
E7 | Solid-state circuit breaker (SSCB) / semiconductor-hybrid CB, 800-1000 VDC — ALTERNATE to fuse+contactor per output | §8.1.3 | ABB / Siemens / Eaton / Atom Power (UL 489I / IEC 60947-10) | Optional | 0 | ea | 4500 | 0 | eval agmt | OPTION per LVDC WP §7.2.4.3: us-class clearing, resettable, current-limiting — addresses tens-of-A/us DC fault rise + selectivity. UL 489I new; IEC 60947-10 publishing soon. Qty 0 baseline (fuse+contactor per Diablo spec).
F — DC OUTPUT CABLES & CONNECTORS (§8.4, App C)
F1 | 100 kW / 125 A output cable assy: 4x 1 AWG W-type single conductors, 5 m, 3W+PE+2 sense, NEC 310.60(C)(4) 65C | §8.4, §14.1 | Custom assembly (industrial cable house) | Custom Fab | 10 | ea | 1400 | 14000 | 6-10 wk | 0.1% V-drop budget @ 5 m (§8.4); 15% design margin (App C). INTEROP NOTE: ORV3 HVDC-LVDC 100kW shelf takes 2x 50kW/62.5A cords (not 1x 100kW) — for interop w/ real shelves use Diablo Option 1 (50kW/63A, 4x 4AWG): set Assumptions B10=50, cable qty doubles automatically.
F2 | HV connector set per cable end: +/-400/COM/PE + 2x LMFB sense, 125 A, latching w/ interlock switch | §8.4, Tbl 13 | Amphenol SurLok Plus / HVC2P / Voltarius as bridge; FCI 10183400/01-series when released | Custom Fab | 20 | set | 350 | 7000 | 8-12 wk | CORROBORATED: ORV3 HVDC-LVDC 100kW shelf spec v1.0.0 (released 2/20/26) names mating shelf-side receptacle Amphenol 10184015-002LF — same 1018xxxx FCI family as Diablo Tbl 13 P/Ns. Pinout confirmed: P1=-400V, P2=COM, P3=+400V, P4=PE, S1/S2. Cable-side P/Ns (10183400/01) still need Amphenol ICC RFQ — design-lock the family. DC-Crosslink per LVDC WP Fig.35; UL 2278 MCS remains the standards-backed alternate. Note: shelf spec glossary defines LMFB = Low-Side MOSFET Bridge; PSKILL short pin = hot-swap arc mitigation.
F3 | Interlock latch switch integration + de-energize logic (SELV within safety time on unplug) | §8.4 | Custom (w/ E5 relay logic) | Custom Fab | 1 | lot | 2000 | 2000 | w/ E1
G — ENERGY STORAGE (§7.2) — OPTIONAL PER SPEC
G1 | CBU supercapacitor shelf, ~15-20 kW class, UL9540A | §7.2.2 | Eaton XLHV / Delta Power Capacitance Shelf / Lite-On 20 kW | Production | 2 | ea | 7500 | 15000 | 8-12 wk | Strongest available-now option. LVDC WP role: sub-ms shock absorber for AI load steps, coordinated w/ BBU (CBU=immediate transients, BBU=sustained). Not a 45-90 s ride-through substitute.
G2 | BBU 4OU, +/-400 V-class, 80 kW, blind-mate, 45-90 s @ 100% load | §7.2.1 | Delta 80 kW embedded BBU class (GTC 2026) | Optional | 13 | ea | 9000 | 117000 | eval agmt | OPTIONAL config — full 100% load backup power-match. Sampling only; 48 V ORV3 BBUs are production but wrong voltage class. Defer to Stage 2 unless required.
H — MANAGEMENT & TELEMETRY (§9, §10.1)
H1 | Rack management controller, Redfish, Ethernet + CANbus/Modbus internal | §9.1-9.3 | OpenBMC-based / Advanced Energy PMC / Legrand controller | Production | 1 | ea | 1200 | 1200 | 4-6 wk | Redfish recommended by spec; in-rack comm to all building blocks shall be implemented.
H2 | Ethernet switch, protocol gateways (CAN/Modbus), comm harnesses | §9 | Stock industrial | Production | 1 | lot | 1800 | 1800 | stock
H3 | Thermal telemetry: inlet/exhaust air temp, component temps, fan tach/fail, busbar-clip thermistors | §10.1, §8.2 | Vishay NTCALUG54A / TDK B57881S0123F000 / JOYIN JAS103G398FB240001RH | Production | 1 | lot | 600 | 600 | stock | Bus-clip thermistor parts per ORV3 HVDC-LVDC shelf spec §4.9: 150C min, 2K 0.1% pull-up to 3.3V, one per +/- contact — satisfies Diablo §8.2 bus clip thermal sensor.
I — SAFETY & COMPLIANCE (§11)
I1 | NRTL field evaluation (IEC/UL 62368-1 path) | §11.1 | UL / Intertek / TUV | Service | 1 | lot | 25000 | 25000 | 12-20 wk | No listed-product path exists for this class — field eval is the realistic route. Engage early.
I2 | DC arc-flash study + labeling (+/-400/800 VDC) | §11.1 | PE consultant | Service | 1 | lot | 8000 | 8000 | 6-10 wk | No DC IEEE 1584 equivalent. Method per LVDC WP §7.6: NFPA 70E Annex D.5 Maximum Power Method (conservative, x3 in-enclosure). Fast clearing keeps IEm well under 1.2 cal/cm2 PPE boundary. NFPA 70 2026 §110.16 permanent labels req. NFPA 70E Art.360: hearing protection where cap energy >100 J (likely w/ CBU). 2029 NEC to formalize — interim OOI + hazard-based risk assessment.
I3 | EMC pre-scan, CISPR 32/35 Class A | §11.2 | EMC test lab | Service | 1 | lot | 12000 | 12000 | 8-12 wk | Incl. ESD, surge, radiated immunity per Tbl 12 targets.
I4 | PPE, 1000 V insulated tools, LOTO hardware | §11.1 | Stock safety supply | Production | 1 | lot | 3000 | 3000 | stock
J — INTEGRATION
J1 | Integration, assembly, wiring, commissioning & test labor | — | In-house / contract | Service | 1 | lot | 35000 | 35000 | — | Protection coordination, GFD commissioning, load-bank validation of droop/transient envelope.
J2 | Misc hardware, fasteners, labels, consumables | — | Stock | Production | 1 | lot | 2500 | 2500 | stock
K — PoC LOAD / IT-SIDE VALIDATION
K1 | DC load bank, +/-400 VDC, 100-250 kW (rental, ~1 month) | §7.3.3 | Avtron/Simplex DC or electronic DC loads | Service | 1 | lot | 12000 | 12000 | 4-8 wk | Validates droop, regulation and dynamic-load envelope (Tbl 6-8) before any real IT load. Program pulse profiles per Diablo Tbl 7/8.
K2 | ORV3 HVDC-LVDC 100 kW power shelf, 1OU (6x 18kW slots, 2x HVDC cords) — representative real load | OCP shelf spec v1.0.0 | Built to Meta OCP spec (released 2/20/2026) | Sampling | 1 | ea | 6000 | 6000 | eval agmt | Ideal end-to-end demo: Diablo rack -> 2x 50kW cords -> shelf -> 48V. Input +/-400 to +/-410 VDC, 2x 62.5A, 537x46.2x867.5mm. >=10 shelves parallel per rack = 1 MW IT rack. Input receptacle Amphenol 10184015-002LF.
K3 | +/-400V-to-48V 18 kW DC PSU modules (populate K2) | OCP 18kW PSU spec | Per Open Rack V3 +/-400V to 48V 18kW PSU spec | Sampling | 6 | ea | 1500 | 9000 | eval agmt | Hot-swap blind-mate; chassis connector Amphenol 10169892-843201SLF. Peak load <=140% <=50ms per shelf spec §4.5.
K4 | 48V resistive load bank for shelf output | — | Stock 48V load | Production | 1 | lot | 3000 | 3000 | 2-4 wk
ALL PRICING IS ROM (BUDGETARY) AS OF JUNE 2026 — NOT QUOTED. Yellow-filled costs carry highest uncertainty (sampling hardware, custom NRE, services). Status legend: green=Production (orderable), yellow=Sampling (eval agreement required), red=Custom Fab, blue=Service, purple=Optional per spec.

## Summary
DIABLO 400 PoC BOM — Cost Summary (ROM)
Section | Description | Ext. Cost ($)
A | Rack Mechanical (§6) | 27500
B | AC Input & AC PDU (§7.1, §8.1.1, App D) | 63020
C | AC/DC Power Shelves & PSUs (§8.2) | 184800
D | ±400VDC Distribution Busbar (§8.3) | 14500
E | DC PDU / Output Protection & Control (§8.1.3) | 52340
F | DC Output Cables & Connectors (§8.4, App C) | 23000
G | Energy Storage (§7.2) — incl. optional BBU | 132000
H | Management & Telemetry (§9) | 3600
I | Safety & Compliance (§11) | 48000
J | Integration | 37500
K | PoC Load / IT-side Validation | 30000
| Subtotal | 616260
| Contingency | 92439
| TOTAL (ROM) | 708699
| Total excluding optional BBU (G2) | 574149